## Sheet1
SRS HVPSU Test Results
Document containing history of tests, results and solutions throughout the development of the SRS HVPSU IOC
Expand cell for further document information: Dates on tests are when formally tested after the creation of the test document, many features were tested and reviewed prior to this then retested for the purpose of the document Features are labelled by numbers such as 3.1 (with 3. being the "voltage monitoring" feature and 3.1 being the more specific "monitored while Idle" which falls under the voltage monitoring heading. Tests may be referred to by either their feature (e.g. 6.2) or the more specific test for the feature (e.g. 6.2.2 would be the second test for feature 6.2) Precursory measures are measures taken before testing to prevent something, some were included in the document for context.
| Feature |  | Precursory measures | Test | Result | Date of test | Solution/notes | Done | Key
| 1.0. Voltage Ramping calculation | [8 empty] | Test worked/completed
| 1.0. | Automatic ramping mode: | [7 empty] | Test failed but now fixed
| 1.0.1 | calculated interval should be a factor of ramp time |  | Attempt ramping with normal cases and edge cases such as prime numbers, manually check if the interval is a factor. | Works as intended | 2025-12-01 |  | ✓ |  | Test failed, not yet fixed
Need another model to test
| 1.0.2 | Interval shouldn't be below 1.5 seconds |  | Attempt to input values that'd calculate interval as below 1.5 (see 1.1.3 for manual mode) | Works as intended | 2025-11-28 |  | ✓
| 1.0.3 | Step size shouldn't be below min step size |  | Attempt to input values that'd calculate step size as below minimum (see 1.1.4 for manual mode) | Works as intended | 2025-11-27 |  | ✓
| 1.0.4 | There should be no divide by zero errors | Interval and ramp time cannot be below 1.5 no matter the device specs. Voltage difference is also is checked for before calculation. | Change minimum step size to 0. | Works as intended | 2025-11-28 |  | ✓
|  |  |  | Input a target voltage equal to present voltage (so that voltage difference is 0) | Works as intended | 2025-11-28
| 1.0.5 | Ramping does not occur if there is an error | There is a check made before calculation which should output an error message if voltage differece is too small. | Input a target voltage where the difference is below minimum step size | Works as intended | 2025-11-28 |  | ✓
| 1.1 | Manual ramping mode::
| 1.1.1 | User can input step size, interval and desired voltage, these values are used and target voltage is reached. |  | Try multiple ramps with various values. | Works as intended | 2025-12-01 |  | ✓
|  |  |  | Try a step size which isn't a factor of desired voltage | Works as intended | 2025-12-01
|  |  |  | Try a step size greater than target voltage. | Works as intended | 2025-12-01
| 1.1.2 | Ramp time is calculated accurately based on user values |  | Try multiple ramps with various values and times, calculate if ramp time is correct and time how long they take. | Works as intended | 2025-12-01 |  | ✓
|  |  |  | Try edge cases where step size is not a factor and therefore a larger step is taken at the end. | Works as intended | 2025-12-01
| 1.1.3 | User cannot input interval below 1.5 secs |  | Attempt to input an interval below 1.5 seconds using ui | Works as intended | 2025-11-28 |  | ✓
|  |  |  | Attempt to input an interval below 1.5 seconds using caput | Allows caput of a value below min | 2025-11-28 | Changed pv to an ao record and added DRVH and DRVL as well as HOPR and LOPR | ✓
[5 empty] | Works as intended | 2025-11-28
| 1.1.4 | User cannot input step size below minimum step size |  | Attempt to input a step size below minimum using ui | Works as intended | 2025-11-27 |  | ✓
|  |  |  | Attempt to input a step size below minimum using caput | Step size allows value below min | 2025-11-27 | Changed pv to an ao record and added DRVH and DRVL as well as HOPR and LOPR | ✓
[5 empty] | Works as intended | 2025-11-27
| 1.1.5 | Ramping cannot occur if there is an error | There is a check made which should output an error message if voltage differece is too small. | Input a target voltage where the difference is below minimum step size. | Works as intended | 2025-11-28 |  | ✓
2.0. Voltage Ramp
| 2.1 | Ramping occurs using ramp settings values |  | See tests 1.0.1 and 1.1.1 | Works as intended | 2025-12-01 |  | ✓
| 2.2 | Start charge button cannot be pressed while high voltage is disabled | Start charge button is disabled when high voltage is off | Disable high voltage and try to start ramping through ui. | Works as intended | 2025-11-28 |  | ✓
|  |  |  | Disable high voltage and try to start ramping through command line. | Goes into ramping state (but doesn't increase voltage due to HV being disabled) | 2025-11-28 | Added a check in the state machine and calculation routine for if HV is disabled | ✓
[5 empty] | Worked as intended except the start charge button in ui would become enabled afterwards | 2025-11-28 | Was previously using 2 separate rules for each reason the button should be disabled, merged into 1 rule
[5 empty] | Works as intended | 2025-11-28
| 2.3 | Ramping stops when a stop ramping button is pressed |  | Attempt to stop ramping using stop ramping button | Works as intended | 2025-11-20 | If stopped during the 1.45 second delay it looks like it increases but it is due to the delay in monitoring | ✓
|  |  |  | Press HV off button while ramping | High voltage was disabled but ramping state was still shown. | 2025-11-19 | Added a step in the HV on/off sequence which sets the ramp active variable to 0 | ✓
[5 empty] | Works as intended | 2025-11-20
| 2.4 | Ramping should take the amount of time specified by the user in "ramp time" |  | Ramp using automatic mode with various values, time how long it takes | Works as intended (allow for slight rounding issues, may take 1 second longer or shorter) | 2025-12-01 |  | ✓
|  |  |  | Ramp using manual mode with various values, time how long it takes | Works as intended | 2025-12-01
| 2.5 | Ramp should stop at desired voltage and not go further |  | Try a step size greater than target voltage in manual mode (see 1.1.1) | Works as intended | 2025-11-28 |  | ✓
| 2.6 | Ramp should not be in a situation where it needs to take a final step under the minimum step size |  | Try ramps where step size is minimum and target voltage is not a multiple of step size. (including where remainder is 1, 1 below minimum step size and exactly minimum step size) | Works as intended | 2025-11-28 |  | ✓
3.0. Voltage monitoring
| 3.1 | Monitored while Idle |  | Camonitor voltage monitor scan field while idle | Works as intended | 2025-11-28 |  | ✓
| 3.2 | Monitored while ramping |  | Camonitor voltage monitor scan field while ramping | Works as intended, OutputVget is processed between 1.45 and 1.48 seconds after HVset | 2025-11-28 |  | ✓
| 3.3 | Pauses for 1.45 seconds after being set to give time for value to stabilize before being read |  | Camonitor voltage monitor scan field alongside HVset, compare timestamps to ensure it is passive for the stabilization period |  | 2025-11-28 |  | ✓
| 3.4 | Display on UI is accurate |  | Compare camonitor of voltage and ui display to the display on front of device | Works as intended | 2025-12-01 |  | ✓
4.0. Voltage graph
| 4.1 | Graph displays voltage accurately |  | Compare graph display to camonitor and display on front of device | Works as intended | 2025-11-04 |  | ✓
| 4.2 | Scales dynamically |  | Change voltage values and check scaling is readable while ramping or idle | Works as intended | 2025-11-04 |  | ✓
| 4.3 | Displays time accurately |  | Check time against camonitor time stamps | Works as intended | 2025-11-27 |  | ✓
5.0. Reset and trip clear
| 5.1 | Reset button safely resets the device |  | Reset using machine compared to device | Works as intended | 2025-12-04 |  | ✓
| 5.2 | Reset button disables HV before resetting |  | Reset while High voltage is on | Works as intended | 2025-11-04 |  | ✓
| 5.3 | Reset button clears trips before resetting |  | Reset while device is tripped. | Works as intended | 2025-11-04 |  | ✓
| 5.4 | Trip clear button clears any trips |  | Simulate or create a trip (7.1) on the device and use trip clear button to clear it | Works as intended | 2025-12-04 |  | ✓
6.0. High voltage enable buttons
| 6.1 | On and off buttons turn high voltage on/off |  | Turn HV on/off using ui and check device to ensure status is correct. | Works as intended | 2025-11-24 |  | ✓
| 6.2 | On/off status is shown on ui |  | See 6.1, ensure status on device is consistent with ui. | Works as intended | 2025-11-24 |  | ✓
|  |  |  | Turn HV off using device, check ui shows new status | Correct status in text but on/off buttons are highlighted incorrectly | 2025-11-24 | Changed button ui rule to be connected to HVON instead of HVenable | ✓
[5 empty] | Works as intended | 2025-11-24
| 6.3 | Enabling voltage doesn't restore previous HV setting |  | Set voltage while HV enabled, then disable then re enable it | Works as intended | 2025-11-04 |  | ✓
7.0. Status poll byte and LEDs
| 7.1 | Status poll byte is regularly and accurately monitored | At first test: All bits of the status poll byte are monitored by ReadbackPoll which scans at 1 second and has a delay of 1.45 seconds after voltage is set. | Individually check each bit and whether the frequency of scanning is adequate (See 6.0, 7.3, 7.4) | HV on/off (See 6.0): Works as intended, only needs a scan of 1 second | 2025-11-24 | ReadbackPoll now scans at 0.5 seconds, Status of stable LED is now linked in the voltage monitor sequence instead so it has the 1.45 second delay. | ✓
[5 empty] | Stable LED(See 7.3): 1.45 second delay necessary, only needs to scan every 1 second | 2025-11-24
[5 empty] | Trip LEDS (See 7.4.1): 1.45 second delay is not adequate for monitoring trips, needs to scan at 0.1-0.5 secs no delay | 2025-11-24
[5 empty] | Works as intended | 2025-12-04
| 7.2 | Ramping LED enables while ramping |  | View LED while ramping vs idle | Works as intended | 2025-11-26 |  | ✓
|  |  |  | View LED after ramping has been interrupted by disabling HV on ui | Device still shows ramping when switched off | 2025-11-19 | Added a link to 'endCharge' in HV on/off sequence | ✓
[5 empty] | Works as intended | 2025-11-19
|  |  |  | View LED after ramping has been interrupted by disabled HV on device | Continues to display "ramping" state |  | Added a check for Hvon status in the ramping state machine | ✓
[5 empty] | Works as intended | 2025-12-01
| 7.3 | Stable LED accurately shows if there's a stable voltage level | At first test: scanned once per second | View LED while ramping normally | Flashes red after Hvset due to expected instability period | 2025-10-02 | Added calc so while ramping, allows a second of instability while still showing green | ✓
[5 empty] | Works as intended | 2025-10-03
|  |  |  | View LED while ramping quickly | Still flashes red after Hvset when ramping quickly | 2025-10-13 | Reworked monitoring so readbackPoll has 1.45 second delay too | ✓
[5 empty] | Works as intended | 2025-11-06
|  |  |  | View LED while purposefully creating an unstable state | Works as intended | 2025-11-06 |  | ✓
| 7.4 | Trip and current limit LEDs accurately detect and show trips that have occurred |  | Create trip event (overvoltage, overcurrent or current limit reached) | LED flashes on for 1-2 seconds then goes back to normal even though device is still tripped | 2025-11-24 | Added mbbi record that stores trips until cleared (see 7.4.2) | ✓
[5 empty] | Trips not detected if within 1.45 second delay period | 2025-11-24 | (See 9.1.2) Now constantly scans at 0.5 secs, stable status now linked to voltage monitor
[5 empty] | LED still flashes on then off despite only processing once | 2025-12-04 | Changed the way TripStatus is processed from the calcout record by removing "PP"
[5 empty] | Works as intended | 2025-12-04
|  |  |  | Use record to simulate trip (set input as from a bi record controlled by a button) | LED is turned on but not turned off when trip clears. | 2025-11-25 | (see 7.4.1) Changed to mbbidirect so each bit can be written to and whole byte can be reset. | ✓
[5 empty] | Works as intended | 2025-11-26
8.0. Voltage and current limits
| 8.1 | Limits are enforced by all necessary PVs |  | Attempt to input target voltage over default voltage limit using ui and caput | Works as intended | 2025-11-19 |  | ✓
|  |  |  | Attempt to input target voltage over a user set voltage limit using ui and caput | Works as intended | 2025-11-19
|  |  |  | Set desired voltage to 20kV, then change maximum voltage to 15kV | desired voltage automatically decreases to new maximum, Works as intended | 2025-11-19
| 8.2 | Limits are, on start, read from a substitutions file dependent on the device |  | Change substitutions file values and see if the new values are used | Works as intended | 2025-11-19 |  | ✓
|  |  |  | Test other models and their substitutions | Works as intended | 2025-12-18 |  | ✓
| 8.3 | Limits are able to be changed within a submenu |  | Open sub menu and change values, see if changed using limit get command to device. (also see 8.1.2) | Works as intended | 2025-11-19 |  | ✓
| 8.4 | Changes are only applied once "apply" is pressed |  | Make changes then close menu without applying them. (also see 8.5.3) | Works as intended | 2025-11-19 |  | ✓
| 8.5 | Limits can be reset to default values in the menu |  | Press reset values button and see if changes reflect substitutions file values | Works as intended | 2025-11-19 |  | ✓
|  |  |  | Repeat after 8.2 with the new substitutions | Works as intended | 2025-11-19 |  | ✓
|  |  |  | Press to reset then close without applying changes (8.4) | Reset values were applied | 2025-11-19 | remove FLNK to apply after reset seq | ✓
[5 empty] | Works as intended | 2025-11-19
9.0. Current monitoring and graph
Hooked device up to Thompson plates to test
| 9.1 | Current is regularly and accurately monitored |  | Check scan field while ramping and idle (see 3.1, 3.2, 3.3) | Scan field works as expected (1 second scan, pause for stabilising) | 2025-11-24 | see 9.1.2 change | ✓
[5 empty] | Scan field works as expected (0.1 second scan, no pause) | 2025-11-24
|  |  |  | Check values against those on the device | Device had some quick spikes that weren't picked up by the 1 second scan as they lasted less than a second or were within the 1.45 second delay period. | 2025-11-24 | Changed scan to .1 second and don't pause for stabilising (no longer link to readback poll (repeat 9.1.1 with new scan) | ✓
[5 empty] | Changes were picked up by device accurately- works as intended | 2025-11-24
| 9.2 | Current is plotted alongside voltage on the graph |  | Ramp device up using various values | Works as intended | 2025-11-24 |  | ✓
| 9.3 | Current trace won't overlap with voltage trace for extended periods of time |  | Run IOC with both current and voltage at 0 or other value where they may overlap | Current and voltage trace overlap at 0. | 2025-11-21 | Used fixed values instead of autoscale to be able to offset the minimum on Y axis from voltage's by a little bit | ✓
[5 empty] | Lines appear one above the other with no gap between, works as intended | 2025-11-21
| 9.4 | There is a separately scaled Y axis that works for all models |  | Repeat 9.2 with different models and values | due to 9.3 fix, Y axis maximum is a fixed value of 1mA which works for all models but isn't dynamic | 2025-11-21 | Used autoscale for dynamic scaling, offset minimum value by small amount to maintain results of 9.3 fix | ✓
[5 empty] | Fixed Y axis values are completely ignored on newer versions of phoebus meaning the graph's scale was -3.5 to 3 instead of 0 to 1. | 2026-01-08
[5 empty] | Works as intended | 2026-01-09
10.0. Polarity
| 10.1 | Polarity is accurately shown on ui |  | Try models PS370 and PS375 and see if display reflects polarity accurately | Works as intended | 2025-12-18 |  | ✓
| 10.2 | Ramping works for either polarity |  | Test ramping with PS370 and PS375 models | Works as intended | 2025-12-18 |  | ✓
| 10.3 | IOC recognises when there is a change in polarity | Currently cannot test due to not having acces to a PS310 or other switchable model | Use model PS310 and switch its polarity, see if IOC recognises it and if ui shows the new polarity value
11.0. Autosave
| 11.1 | Configurations and values can be saved when IOC is reloaded |  | Try saving a configuration and loading it both while the IOC is running in the same instance, and after exiting and restarting | Works as intended | 2025-12-11 |  | ✓
| 11.2 | Ramping configurations can be saved under a user chosen name |  | repeat 11.1 with user chosen names | Works as intended | 2025-12-11 |  | ✓
| 11.3 | Previously saved configurations can be loaded in and used |  | see 11.1 | Works as intended | 2025-12-11 |  | ✓
12.0. Deployment
| 12.1 | IOC is able to be deployed |  | Deploy IOC and try doing functions such as ramping | Errors when trying to deploy, did not deploy. | 2026-01-06 | Prefix contained a colon which caused an error so it was removed and put into the PV name instead, Prefix was in two parts "$(P)$(R)" which caused some issues so it was changed to "$(DEVICE)" | ✓
[5 empty] | Works as intended | 2026-01-06
|  |  |  | Deploy a second instance of the IOC | Works as intended | 2026-01-06 |  | ✓